Title: An Firma
Author: MD
Last saved by: Hagenlocher, Joachim

Windancer Modbus weather station

Weather station for Modbus. Recording of brightness (3 brightness sensors east/south/west, twilight detection), wind speed (cup anemometer), precipitation (heated sensor), temperature.
Data output via RS485 interface with Modbus RTU protocol. The device works as a Modbus server, the Modbus client reads the measured values with "Function 04h (Read Input Registers)". RS485 bus load 1/8 Unit Load, RS485 driver power min. 2.4 V at 54 Ohm bus load.
Outdoor installation, surface-mounted or on pole. Housing plastic. Degree of protection IP44. Ambient temperature -25...50 °C, storage temperature -30...70 °C. Voltage 24 V DC SELV ±10 % (SELV power supply unit according to EN 61558), current consumption 70 mA, polarity-independent connection of the supply voltage. Connection via plug-in terminals. Measuring range temperature -25...50 °C, wind 2...30 m/s, brightness 0...150000 Lux. Dimensions 113 × 101 × 225 (W x H x D in mm).
Colour: white/translucent.

Manufactured by: Elsner Elektronik (www.elsner-elektronik.de)
Type: 30176 Windancer Modbus

Windancer GPS Modbus weather station

Weather station for Modbus. Recording of brightness (3 brightness sensors east/south/west, twilight detection), wind speed (cup anemometer), precipitation (heated sensor), temperature. Integrated GPS receiver for the output of world time UTC, date and location coordinates (longitude, latitude) as well as for the calculation of the sun's position (azimuth, elevation).
Data output via RS485 interface with Modbus RTU protocol. The device works as a Modbus server, the Modbus client reads the measured values with "Function 04h (Read Input Registers)". RS485 bus load 1/8 Unit Load, RS485 driver power min. 2.4 V at 54 Ohm bus load.
Outdoor installation, surface-mounted or on pole. Housing plastic. Degree of protection IP44. Ambient temperature -25...50 °C, storage temperature -30...70 °C. Voltage 24 V DC SELV ±10 % (SELV power supply unit according to EN 61558), current consumption 70 mA, polarity-independent connection of the supply voltage. Connection via plug-in terminals. Frequency range GPS 1559...1610 MHz. Measuring range temperature -25...50 °C, wind 2...30 m/s, brightness 0...150000 Lux. Dimensions 113 × 101 × 225 (W x H x D in mm).
Colour: white/translucent.

Manufactured by: Elsner Elektronik (www.elsner-elektronik.de)
Type: 30177 Windancer GPS Modbus

Elsner Elektronik GmbH | Sohlengrund 16 | 75395 Ostelsheim | www.elsner-elektronik.de	

Stand 31.08.2026